A.C. CURRENT TRANSDUCER

SERIES 1006

PART                     INPUT             OUTPUT            PART                INPUT             OUTPUT

NUMBER.             CURRENT       IMPEDANCE     NUMBER          CURRENT       IMPEDANCE

1006-5	0 TO 5	9	1006-200	0 TO 200	………0.22

1006-10	0 TO 10	4.5	1006-250	0 TO 250	.0.18

1006-20	0 TO 20	2.2	1006-300	0 TO 300	…0.22

1006-25	0 TO 25	1.7	1006-350	0 TO 350	0.2

1006-30	0 TO 30	1.55	1006-400	0 TO 400	0.17

1006-35	0 TO 35	1.4	1006-500	0 TO 500	0.13

1006-50	0 TO 50	0.88	1006-600	0 TO 600	0.11

1006-75	0 TO 75	0.61	1006-800	0 TO 800	0.12

1006-100	……..0 TO 100	0.45	1006-1000	……..0 TO 1000	0.1

1006-150….	..0 TO 150	0.3	1006-1200……..0 TO 1200………….0.1

INPUT

RANGE		Aac See Table

FREQUENCY		47 to 63Hz (Optional Model Available)	 *

OVERLOAD CONTINUOUS		500Aac or two X FS which ever is greater

OVERLOAD TRANSIENT	   3000Aac for 10 cycle.

OUTPUT

VOLTAGE SIGNAL		0 to 5Vdc FS (Full Scale)**

ACCURACY		 0.5% FS

RIPPLE (RMS)		10mV RMS typical

RESPONSE (10 to 90%)	 	200m-sec typical

IMPEDANCE		K Ohms max.  See Table

TEMPERATURE COEFFICIENT		±0.02% FS/°C max.

REPEATABILITY		±0.1% FS

VOLTAGE SIGNAL @ OVERLOAD		10Vdc max.

VOLTAGE SIGNAL LINEAR TO		6Vdc (120% FS)

POWER SUPPLY

SUPPLY VOLTAGE 		None, Self Excited

ENVIRONMENTAL AND PHYSICAL CHARACTERISTICS

OPERATING TEMPERATURE RANGE		-40 to +85°C

STORAGE TEMPERATURE RANGE		-55 to +85°C

ISOLATION		Input/Output/Case

CONDUCTOR CABLE VOLTAGE		1.5KV max. (5KV with Insul. Cable)

CASE 		Molded Plastic Meets UL Flammability

Rating 94V- 0

WEIGHT 		1.2 lbs. max.

*  Add suffix -400 to part number for 400Hz operation.

** 4 to 20mA Two Wire Output Option Available as 1006X.

Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

TERMINALS:

5-40 SCREWS, 3/8” CENTER TO CENTER SPACING, ACCEPTS WIRE SIZES UP TO 14 AWG AND WIRE LUGS UP TO 9/32” WIDE.

Drawing Number	Rev.

700-1006	M

AAC