AC VOLTAGE TRANSDUCER

PART NUMBER 101M3-150

INPUT VOLTAGE

RANGE		90 to 150Vac RMS

FREQUENCY		60Hz

BURDEN		1 Va Typical

OVERVOLTAGE CAPABILITY		200 Vac max.

OUTPUT SIGNAL

VOLTAGE SIGNAL (V min. to V max.)		0 to 5Vdc FS (Full Scale)

ACCURACY		±0.5% FS (±25mV)

RESPONSE		Within 0.5 cycle of input frequency

RIPPLE		1% 50mV RMS max.

TEMPERATURE COEFFICIENT		± 0.08% FS/°C max. (±4mVdc /°c)

OUTPUT IMPEDANCE		2.5 K-Ohms max.

ENVIRONMENTAL AND PHYSICAL CHARACTERISTICS

OPERATING TEMPERATURE RANGE		-40 to +85°C

STORAGE TEMPERATURE RANGE		-55 to +100°C

DIELECTRIC STRENGTH		300 V-RMS

INSULATION RESISTANCE		100 M Ohms @ 500Vdc

VIBRATION		Operating, meet or exceed Method 201A of

MIL-STD-202F and Method 514.3 cat. 4 of   MIL-STD-810C.

SHOCK		Operating:  50g, 11 m-sec half sine pulse

(meet or exceed method 213B, Condition A

of MIL-STD-202F)

MOISTURE RESISTANCE		Meet or exceed Method 106 of MIL-STD-202F

and Method 507.2 proc. 1 of MIL-STD-810C.

OPERATING HUMIDITY		0% to 95% RH

WEIGHT		20 oz. max.

Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

Drawing Number	Rev.

700-101M3	G

AAC

TERMINAL IDENTIFICATION

1.   A.C. INPUT HI

2.   A.C. INPUT LO

3.   CASE GROUND

4.   OUTPUT (RTN)

5.   OUTPUT (+)