fo

Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

AC VOLTAGE SENSOR

MODEL 105

PRESET RANGE (VMAX TO VMIN)		MODEL

390 to 490 VRMS			 -490

455 to 505 VRMS			 -505

430 to 530 VRMS                                                    -530

400 to 560 VRMS			 -560

INPUT LINE FREQUENCY		57 to 63Hz

EXCITATION		Self-excited

BURDEN		1Va Typical

OUTPUT FOR PRESET RANGE		0 to 5Vdc

OUTPUT IMPEDANCE		3K Ohms Max.

RESPONSE		Within 1 Cycle of Input Frequency

RIPPLE		50mV RMS

SUPPRESSION VOLTAGE ACCURACY		± .25% of V Min.

RANGE ACCURACY		± 0.5% F.S. Max.

TEMPERATURE COEFFICIENT		± .08% F.S. per °C

TEMPERATURE RANGE		-40 to +85°C

WEIGHT		20oz. Max.

* OTHER PRESET RANGES AVAILABLE

TERMINAL IDENTIFICATION

1.  A.C. INPUT HI

2.  A.C. INPUT LO

3.  CASE GROUND

4.  OUTPUT RETURN

5.  OUTPUT POSITIVE

Drawing Number	Rev.

700-105	L

AAC