AC VOLTAGE TRANSDUCER

SERIES 108

PART                          INPUT VOLTAGE	                          CONTINUOUS

NUMBER	             RANGE Vac		           OVERLOAD Vac

108-50		0 to 50	100

108-130		0 to 130	180

108-150		0 to 150	200

108-270		0 to 270	380

108-300		0 to 300	410

108-500		0 to 500	700

108-600		0 to 600	800

INPUT

VOLTAGE RANGE		See Table

FREQUENCY		60Hz (Optional Model Available) *

FREQUENCY RANGE		57 to 63Hz

BURDEN		3mA max.

OVERLOAD Vac		See Table

OUTPUT

VOLTAGE SIGNAL		0 to +5Vdc FS (Full Scale)

4 to 20mA Output Models Available

ACCURACY		±0.5% FS (±25mV)

RESPONSE (0 to 90%)		300 m-sec max.

RIPPLE		25mV RMS max.

TEMPERATURE COEFFICENT		±0.02% FS/°C max.

REPEATABILITY		± 0.1% FS

OUTPUT IMPEDANCE		4000 Ohms max.

POWER SUPPLY

SUPPLY VOLTAGE		Self excited

ENVIRONMENTAL AND PHYSICAL CHARACTERISTICS

OPERATING TEMPERATURE RANGE		- 40° C to +85°C

STORAGE TEMPERATURE RANGE		- 55°C to +85°C

INSULATION RESISTANCE		200 M-Ohms (all terminals to case)

MOISTURE RESISTANCE	 Will meet Method 106 of MIL-STD

-202 & Method 507.1, Proc.1 of

MIL-STD-810.

DIELECTRIC STRENGTH		1000V RMS

WEIGHT		10 oz. max.

Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

TERMINAL IDENTIFICATION

BARRIER                                           CONNECTOR

1              AC VOLTAGE INPUT            A

2              AC VOLTAGE INPUT            B

3              OUTPUT (+)     	C

4              OUTPUT (RTN)  	D

SPARE                                  E

CASE GROUND                    F

Drawing Number	Rev.

700-108	R

AAC

TERMINAL SCREWS 5-40  3/8 CENTER TO CENTER

WIRE SIZES TO 14 AWG  WIRE LUGS TO .281 WIDE.

* Optional Models

ADD SUFFIX -50 TO MODEL NO. FOR 50Hz OPERATION.

ADD SUFFIX -400 TO MODEL NO. FOR 400Hz OPERATION.

ADD SUFFIX –4000 TO MODEL NO. FOR 4000Hz OPERATION.

CONNETOR

OPTION

ADD “-C” TO

PART NO.

CONNECTOR P/N

PT02E-10-6P-023 OR EQUIV.

MATING CONNECTOR

PT06A-10-6S