Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

AC CURRENT TRANSDUCER

SERIES S383L

4 TO 20mA 2 WIRE LOOP OPERATION

PART NO.	INPUT RANGE	PART NO.	INPUT RANGE

S383L-50	 0 to 50mA	S383L-250		0 to 250mA	         	S383L-100	 0 to 100mA	S383L-500		0 to 500mA

S383L-200		0 to 200mA	S383L-1A		0 to 1A

INPUT

RANGE		Aac See Table

FREQUENCY		50 to 60 Hz

OVERLOAD CONTINUOUS		250Aac

OVERLOAD TRANSIENT		100 Times Range For 250m-sec.

OUTPUT

CURRENT SIGNAL		4 to 20mAdc FS (Full Scale)

ACCURACY		0.5% FS or ±0.1mA max. (Over Temperature Range)

RIPPLE		0.25% FS (0.05 mA RMS)

RESPONSE (10 to 90%)	 	100mS max.

LOAD RESISTANCE (RL)		250 Ohms Nominal

LOAD RESISTANCE RANGE		0 to 1400 Ohms (See Note)

CURRENT SIGNAL @ OVERLOAD		30mA TYP.

PROTECTION		Reverse Polarity Protected

POWER SUPPLY (PS)

SUPPLY VOLTAGE 		15Vdc Nominal

CURRENT DRAIN		20mA

SUPPLY VOLTAGE RANGE		7 to 35Vdc

ENVIRONMENTAL AND PHYSICAL CHARACTERISTICS

OPERATING TEMPERATURE RANGE		-40 to +85°C

STORAGE TEMPERATURE RANGE		-40 to +85°C

ISOLATION		Input/Output/Case

INSULATION RESISTANCE		200 M-Ohms @ 500Vdc

INPUT CONDUCTOR VOLTAGE		1.5KV max. (5KV max. with insulated cable)

CASE **		Aluminum type 1100-0 (finish corvel lava black 20-7042HY

polyester powder coat)

WEIGHT 		10 oz. Max.

NOTE:

MINIMUM DC SUPPLY VOLTAGE = 7V + .02 (RL)

RL = ANY VALUE BETWEEN 0 AND 1400 OHMS.

TERMINAL SCREWS:

5-40 SCREWS, 3/8” CENTER TO CENTER SPACING ACCEPTS WIRE SIZES UP TO 14 AWG.  AND WIRE LUGS UP TO 9/32 WIDE.

Drawing Number	Rev.

700-S383L-1003AM2	E

AAC

TERMINAL IDENTIFICATION

1.  OUTPUT (+)

2.  OUTPUT (RTN)