Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

DC CURRENT LEVEL DETECTOR

PART NUMBER S680

INPUT

RANGE 	 	0 to ± 1000Adc (Continuous)

OVERLOAD / TRANSIENT		± 2004A RMS (1 min)

± 1635A RMS (30 min)

± 2960A Peak (5 sec.)

TRIP POINT SETTING

SET POINT		±3Adc (±10%)

TRIP POINT DELAY (TYPICAL)  		350 m-sec. After input (Absolute Value)	                                              Exceeds Trip Point

ADJUSTMENT RANGE		Field Adjustable ±3 to ±5Adc

RESET POINT SETTING

RESET POINT…………………………….    One Amp (Absolute Value) Below Trip Point

RESET POINT DELAY (TYPICAL)……...   10 Sec. After Input  (Absolute Value) Decreases

Below Reset Point

OUTPUT RELAY (Solid State)

RELAY CONTACT (SPST)		Contacts Close at and above trip point

CONTACT RESISTANCE		On 25 Ohms Max, Off 500M Ohms Min.

DIELECTRIC STRENGTH 		3.3KV RMS 60Hz

CURRENT LIMIT PROTECTION		Automatically Limits Contact Current to 370mA

OPEN CIRCUIT VOLTAGE………………   200Vdc OR Peak Max

DUTY CYCLE………………………………  Number Of “Change Of State” Operations Is                	    Unlimited.

POWER SUPPLY

SUPPLY VOLTAGE 		+25 to 45Vdc

CURRENT DRAIN		25mA max.

TRANSIENT PROTECTION		±60V Peak (30sec.); ±100V Peak (2m sec.)

ENVIRONMENTAL AND PHYSICAL CHARACTERISTICS

OPERATING TEMPERATURE		-25°C to +75°C

STORAGE TEMPERATURE		-40°C to +85°C

SHOCK & VIBRATION 		IAW ADTRANZ Doc. ABB-ES-091291-1

OPERATING HUMIDITY  		0 to 95% Relative Humidity

INSULATION RESISTANCE 		500 M-ohms @ 500Vdc

DIELECTRIC STRENGTH 		3.3Kv RMS 60Hz

PRIMARY BAR VOLTAGE 		2Kv RMS max.

CASE		Molded Plastic (GE Lexan) Meets UL

Flammability Rating 94 V-0

WEIGHT 		6.5 lbs.  max.

NOTE:

1. MOLDED TERMINAL BLOCK WITH 6-32 TERMINAL SCREWS, 3/8 IN.
    CENTER TO CENTER SPACING.  ACCEPTS WIRE SIZES TO 14 AWG

AND WIRE LUGS UP TO 9/32 IN. WIDE. TORQUE 8 IN-LB MAX.

2. REFERENCE DOCUMENT NO. E301-005.RFP (XIZ).

3. RECOMMENDED MOUNTING HARDWARE #8 SCREW, #8 SPLIT             
    LOCKWASHER AND #8 FLAT WASHER.
    TORQUE MAXIMUM 18 IN-LB.

4. AVAILABLE WITH OR WITHOUT THE BUS BAR.

Drawing Number	Rev.

700-S680	F

AAC