O

Dimensions in Inches,   Tolerances:  .XX  .03    .XXX   .010

DC CURRENT TRANSDUCER

# SERIES S966

# REMOVEABLE YOKE TYPE

# PART	CURRENT	PART	CURRENT	NUMBER	RANGE	NUMBER	RANGE

S966-500	0 to 500	S966-750	0 to 750

S966-1000	0 to 1000	S966-1500	0 to 1500

S966-2000	0 to 2000	S966-2500	0 to 2500

S966-3000	0 to 3000	S966-3500	0 to 3500

S966-4000	0 to 4000	S966-5000	0 to 5000

##### INPUT CURRENT

RANGE		Adc (See Table)

OVERLOAD 		10kAdc

## OUTPUT

VOLTAGE SIGNAL		0 to 5Vdc FS (Full Scale)

ACCURACY (Over Temperature Range)		%1 FS

RESPONSE (10 to 90%)	 	200 u-sec. max.

OUTPUT IMPRDANCE	    20 Ohms max.

VOLTAGE SIGNAL @ OVERLOAD 		6.5Vdc typ.

PROTECTION	    Short CKT.

POWER SUPPLY

SUPPLY VOLTAGE 		+11Vdc to +32Vdc

CURRENT DRAIN		20mAdc max.

PROTECTION	    Reverse polarity protected

TRANSIENT PROTECTION	    ±40V (T<10mS)

##### ENVIRONMENTAL AND PHYSICAL CHARACTERISTICS

OPERATING TEMPERATURE RANGE	   -40 to +85°C

STORAGE TEMPERATURE RANGE	   -45 to +91°C

HUMIDITY (Operating)	    0% to 95%RH

ISOLATION	    Input to output 5Kv RMS 60Hz

SHOCK		50g 11m-sec. half sine pulse

INSULATION RESISTANCE		500 M-Ohms @ 500Vdc

DIELECTRIC STRENGTH	    5Kvac rms input to output

CASE MATERIAL		Molded Plastic meets UL flammability

rating 94V-O (color light gray)

WEIGHT 		24 oz. Max.

### NOTE: INTERNAL CIRCUITRY SEALED  MAKING TRANSDUCER WATER SPRAY RESISTANT

YOKE CAPTIVE SCREWS: 8-32 SLOT

TORQUE: 2 IN-LB CAUTION DO NOT EXCEED

SCREWDRIVER: 7/32” SLOTTED HEAD

1 ½” MIN SHAFT LENGTH

Drawing Number	Rev.

700-S966	B

AAC

YOKE CAPTIVE SCREWS: 8-32 SLOT

TORQUE: 2 in-lb CAUTION DO NOT EXCEED.

SCREWDRVIER: 7/32” SLOTTED HEAD

1½” MIN SHAFT LENGTH

RECOMMENDED MOUNTING SCREWS: 10-32 x ¼” MIN;

TORQUE: 5lb-in; FLAT AND LOCK WASHERS.

#### CONNECTOR

P/N PT02E-10-6P-023

MATING CONNECTOR

PT06-10-6S OR EQUIV

### CONNECTOR

### IDENTIFICATION

1.	SIGNAL OUTPUT (+)

2.	OUTPUT (RTN)

3.	SUPPLY VOLTAGE (+)

4.	SUPPLY VOLTAGE (RTN)

5.	SPARE

6.	SPARE

Terminal 2 & 4 are common